## Output (W)
|  |  | Hudevad A/S |  |  |  | Language:
|  |  | Saltgade 11 |  |  |  | Enter temperature set
|  |  | DK-6760 Ribe |  |  |  | Flow temperature |  |  | Return temperature |  |  | Room temperature |  |  | ∆T
[7 empty] | Tf |  |  | Tr |  |  | Ti |  |  | dTln
[7 empty] | 70 |  |  | 40 |  |  | 20 |  |  | 35
www.hudevad.com
[7 empty] | Reduction factor * [%] |  |  | 0%
Temperature set | P5V/P5KV/P5V-D/P5KV-D | [15 empty] | Temperature set | P5V/P5KV/P5V-D/P5KV-D | [7 empty] | RADIATOR DATA
70/40-20 | [16 empty] | 70/40-20 | [49 empty] | /
-
Length [mm] | 300 |  |  |  | 400 |  |  |  | 500 |  |  |  | 600 |  |  |  | Length [mm] | 700 | 600 |  |  | 1000 |  | 700 |  |  | P5V |  |  |  | P5KV |  |  |  | P5V-D |  |  |  | P5KV-D |  |  |  | P5V | [5 empty] | P5KV | [5 empty] | P5V-D | [5 empty] | P5KV-D
Type | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | Type | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | Height [mm] | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m
Height [mm] | Single |  | Double |  | Single |  | Double |  | Single |  | Double |  | Single |  | Double |  | Height [mm] | Single | Single | Double | #REF! | Single | Single | Double | #REF! | [17 empty] | Height [mm] | n | W/m (75/65-20) | Tillæg | KG/m | L/m | Height [mm] | n | W/m (75/65-20) | Tillæg | KG/m | L/m | Height [mm] | n | W/m (75/65-20) | Tillæg | KG/m | L/m | Height [mm] | n | W/m (75/65-20) | Tillæg | KG/m | L/m |  | Stamdata
800 | 171.2401 | 212.3847 | 284.4491 | 389.8465 | 228.3201 | 283.1796 | 379.2654 | 519.7954 | 285.4001 | 353.9745 | 474.0818 | 649.7442 | 342.4801 | 424.7694 | 568.8981 | 779.693 | 800 | 399.5602 | 495.5643 | 663.7145 | 909.6419 | 570.8002 | 707.9491 | 948.1635 | 1299.4884 | 800 | 1.25 | 891.48 | 21.52 | 2.16 | 1.25 | 1105.68 | 28.8 | 2.16 | 1.26 | 1486.14 | 43.04 | 4.32 | 1.27 | 2044.08 | 57.6 | 0 | 800 | 1.25 | 874 | 891.48 | 21.52 | 2.16 | 800 | 1.25 | 1084 | 1105.68 | 28.8 | 2.16 | 800 | 1.26 | 1457 | 1486.14 | 43.04 | 4.32 | 800 | 1.27 | 2004 | 2044.08 | 57.6 | 4.32
900 | 189.7552 | 234.8183 | 314.5144 | 425.0572 | 253.0069 | 313.0911 | 419.3525 | 566.7429 | 316.2586 | 391.3639 | 524.1906 | 708.4287 | 379.5103 | 469.6367 | 629.0287 | 850.1144 | 900 | 442.762 | 547.9095 | 733.8669 | 991.8001 | 632.5172 | 782.7278 | 1048.3812 | 1416.8573 | 900 | 1.25 | 987.87 | 24.21 | 2.43 | 1.25 | 1222.47 | 32.4 | 2.43 | 1.26 | 1643.22 | 48.42 | 4.86 | 1.27 | 2228.7 | 64.8 | 4.86 | 900 | 1.25 | 968.5 | 987.87 | 24.21 | 2.43 | 900 | 1.25 | 1198.5 | 1222.47 | 32.4 | 2.43 | 900 | 1.26 | 1611 | 1643.22 | 48.42 | 4.86 | 900 | 1.27 | 2185 | 2228.7 | 64.8 | 4.86 |  | 3 | [11 empty] | Produkt type
1000 | 208.2703 | 257.252 | 344.5797 | 458.6292 | 277.6937 | 343.0026 | 459.4396 | 611.5055 | 347.1171 | 428.7533 | 574.2995 | 764.3819 | 416.5405 | 514.5039 | 689.1594 | 917.2583 | 1000 | 485.9639 | 600.2546 | 804.0193 | 1070.1347 | 694.2342 | 857.5066 | 1148.5989 | 1528.7638 | 1000 | 1.25 | 1084.26 | 26.9 | 2.7 | 1.25 | 1339.26 | 36 | 2.7 | 1.26 | 1800.3 | 53.8 | 5.4 | 1.28 | 2413.32 | 72 | 5.4 | 1000 | 1.25 | 1063 | 1084.26 | 26.9 | 2.7 | 1000 | 1.25 | 1313 | 1339.26 | 36 | 2.7 | 1000 | 1.26 | 1765 | 1800.3 | 53.8 | 5.4 | 1000 | 1.28 | 2366 | 2413.32 | 72 | 5.4 |  | language | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
1100 | 226.2955 | 279.0978 | 373.8641 | 491.9699 | 301.7274 | 372.1304 | 498.4854 | 655.9599 | 377.1592 | 465.163 | 623.1068 | 819.9498 | 452.591 | 558.1956 | 747.7281 | 983.9398 | 1100 | 528.0229 | 651.2282 | 872.3495 | 1147.9298 | 754.3184 | 930.326 | 1246.2136 | 1639.8997 | 1100 | 1.25 | 1178.1 | 29.59 | 2.97 | 1.25 | 1452.99 | 39.6 | 2.97 | 1.26 | 1953.3 | 59.18 | 5.94 | 1.28 | 2588.76 | 79.2 | 5.94 | 1100 | 1.25 | 1155 | 1178.1 | 29.59 | 2.97 | 1100 | 1.25 | 1424.5 | 1452.99 | 39.6 | 2.97 | 1100 | 1.26 | 1915 | 1953.3 | 59.18 | 5.94 | 1100 | 1.28 | 2538 | 2588.76 | 79.2 | 5.94 |  | Dansk | 1 | Saltgade 11 | DK-6760 Ribe | Tel.: +45 7542 0255 | www.rio.dk | www.hudevad.dk | Indtast temperatursæt | Fremløbstemperatur | Returtemperatur | Rumtemperatur | Reduceringsfaktor * [%] | P5 / P5K + P5-D / P5K-D | Højde [mm] | Type | Længde [mm] | Temperatursæt | *Reduceringsfaktor anvendes ved reduktion af varmeydelsen, f.eks. hvor radiatorer skal monteres i grav eller under loft | Enkelt | Dobbelt | RADIATOR DATA
1200 | 243.4509 | 300.9437 | 401.7131 | 525.3107 | 324.6012 | 401.2582 | 535.6175 | 700.4142 | 405.7515 | 501.5728 | 669.5218 | 875.5178 | 486.9018 | 601.8873 | 803.4262 | 1050.6213 | 1200 | 568.0521 | 702.2019 | 937.3306 | 1225.7249 | 811.503 | 1003.1455 | 1339.0437 | 1751.0355 | 1200 | 1.26 | 1271.94 | 32.28 | 3.24 | 1.25 | 1566.72 | 43.2 | 3.24 | 1.27 | 2106.3 | 64.56 | 6.48 | 1.28 | 2764.2 | 86.4 | 6.48 | 1200 | 1.26 | 1247 | 1271.94 | 32.28 | 3.24 | 1200 | 1.25 | 1536 | 1566.72 | 43.2 | 3.24 | 1200 | 1.27 | 2065 | 2106.3 | 64.56 | 6.48 | 1200 | 1.28 | 2710 | 2764.2 | 86.4 | 6.48 |  | Deutsch | 2 | Saltgade 11 | DK-6760 Ribe | Tel.: +45 7542 0255 |  | www.hudevad.com | Temperatursatz eingeben | Vorlauftemperatur | Rücklauftemperatur | Raumtemperatur | Reduktionsfaktor * [%] | P5 / P5K + P5-D / P5K-D | Bauhöhe [mm] | Typ | Baulänge [mm] | Temperatursatz | *Der Reduktionsfaktor wird für die Reduzierung der Wärmeleistung verwendet, z.B. wenn Heizkörper in Gräben oder unter Decken zu montieren sind | Einlagig | Doppellagig | HEIZKÖRPER DATEN
1300 | 261.0215 | 322.2997 | 430.1151 | 557.1976 | 348.0287 | 429.7329 | 573.4868 | 742.9301 | 435.0359 | 537.1661 | 716.8585 | 928.6627 | 522.0431 | 644.5994 | 860.2302 | 1114.3952 | 1300 | 609.0503 | 752.0326 | 1003.6019 | 1300.1277 | 870.0718 | 1074.3323 | 1433.717 | 1857.3253 | 1300 | 1.26 | 1363.74 | 34.97 | 3.51 | 1.25 | 1677.9 | 46.8 | 3.51 | 1.27 | 2255.22 | 69.94 | 7.02 | 1.28 | 2931.99 | 93.6 | 7.02 | 1300 | 1.26 | 1337 | 1363.74 | 34.97 | 3.51 | 1300 | 1.25 | 1645 | 1677.9 | 46.8 | 3.51 | 1300 | 1.27 | 2211 | 2255.22 | 69.94 | 7.02 | 1300 | 1.28 | 2874.5 | 2931.99 | 93.6 | 7.02 |  | English | 3 | Record Hall Business Ctr, Rm 215 - 16-16A Baldwin Gardens | Hatton Garden, London EC1N 7RJ | Tel.: +44 (0) 2476 88 1200 |  | www.hudevad.com | Enter temperature set | Flow temperature | Return temperature | Room temperature | Reduction factor * [%] | P5 / P5K + P5-D / P5K-D | Height [mm] | Type | Length [mm] | Temperature set | *The reduction factor is used for heat output reduction, e.g. when radiators are to be installed in trenches or under ceilings | Single | Double | RADIATOR DATA
1400 | 277.6003 | 343.6557 | 458.5171 | 586.9872 | 370.1337 | 458.2076 | 611.3561 | 782.6495 | 462.6671 | 572.7595 | 764.1951 | 978.3119 | 555.2006 | 687.3114 | 917.0342 | 1173.9743 | 1400 | 647.734 | 801.8633 | 1069.8732 | 1369.6367 | 925.3343 | 1145.519 | 1528.3903 | 1956.6239 | 1400 | 1.27 | 1455.54 | 37.66 | 3.78 | 1.25 | 1789.08 | 50.4 | 3.78 | 1.27 | 2404.14 | 75.32 | 7.56 | 1.29 | 3099.78 | 100.8 | 7.56 | 1400 | 1.27 | 1427 | 1455.54 | 37.66 | 3.78 | 1400 | 1.25 | 1754 | 1789.08 | 50.4 | 3.78 | 1400 | 1.27 | 2357 | 2404.14 | 75.32 | 7.56 | 1400 | 1.29 | 3039 | 3099.78 | 100.8 | 7.56 |  | François | 4 | Plomb'Art | Kim Staeger-Holst | Tel.: +33 180 815310 |  | www.hudevad.com
1500 | 294.9138 | 364.6199 | 486.4327 | 617.6017 | 393.2184 | 486.1598 | 648.577 | 823.4689 | 491.523 | 607.6998 | 810.7212 | 1029.3361 | 589.8277 | 729.2398 | 972.8655 | 1235.2033 | 1500 | 688.1323 | 850.7797 | 1135.0097 | 1441.0705 | 983.0461 | 1215.3996 | 1621.4425 | 2058.6722 | 1500 | 1.27 | 1546.32 | 40.35 | 4.05 | 1.25 | 1898.22 | 54 | 4.05 | 1.27 | 2550.51 | 80.7 | 8.1 | 1.29 | 3261.45 | 108 | 8.1 | 1500 | 1.27 | 1516 | 1546.32 | 40.35 | 4.05 | 1500 | 1.25 | 1861 | 1898.22 | 54 | 4.05 | 1500 | 1.27 | 2500.5 | 2550.51 | 80.7 | 8.1 | 1500 | 1.29 | 3197.5 | 3261.45 | 108 | 8.1 |  | Norsk | 5 | Saltgade 11 | DK-6760 Ribe | Tel.: +45 7542 0255 |  | www.hudevad.com
1600 | 312.2274 | 385.5841 | 514.3484 | 648.2162 | 416.3032 | 514.1121 | 685.7979 | 864.2882 | 520.379 | 642.6401 | 857.2473 | 1080.3603 | 624.4547 | 771.1681 | 1028.6968 | 1296.4323 | 1600 | 728.5305 | 899.6961 | 1200.1463 | 1512.5044 | 1040.7579 | 1285.2802 | 1714.4946 | 2160.7205 | 1600 | 1.27 | 1637.1 | 43.04 | 4.32 | 1.25 | 2007.36 | 57.6 | 4.32 | 1.27 | 2696.88 | 86.08 | 8.64 | 1.29 | 3423.12 | 115.2 | 8.64 | 1600 | 1.27 | 1605 | 1637.1 | 43.04 | 4.32 | 1600 | 1.25 | 1968 | 2007.36 | 57.6 | 4.32 | 1600 | 1.27 | 2644 | 2696.88 | 86.08 | 8.64 | 1600 | 1.29 | 3356 | 3423.12 | 115.2 | 8.64 |  | Svenska | 6 | Saltgade 11 | DK-6760 Ribe | Tel.: +45 7542 0255 |  | www.hudevad.com
1700 | 329.1518 | 406.0584 | 541.7777 | 677.9615 | 438.8691 | 541.4112 | 722.3703 | 903.9486 | 548.5864 | 676.764 | 902.9629 | 1129.9358 | 658.3037 | 812.1168 | 1083.5554 | 1355.9229 | 1700 | 768.021 | 947.4696 | 1264.148 | 1581.9101 | 1097.1728 | 1353.5281 | 1805.9257 | 2259.8716 | 1700 | 1.27 | 1725.84 | 45.73 | 4.59 | 1.25 | 2113.95 | 61.2 | 4.59 | 1.27 | 2840.7 | 91.46 | 9.18 | 1.29 | 3580.2 | 122.4 | 9.18 | 1700 | 1.27 | 1692 | 1725.84 | 45.73 | 4.59 | 1700 | 1.25 | 2072.5 | 2113.95 | 61.2 | 4.59 | 1700 | 1.27 | 2785 | 2840.7 | 91.46 | 9.18 | 1700 | 1.29 | 3510 | 3580.2 | 122.4 | 9.18
1800 | 344.8442 | 426.5328 | 567.1804 | 705.1871 | 459.7922 | 568.7104 | 756.2406 | 940.2494 | 574.7403 | 710.888 | 945.3007 | 1175.3118 | 689.6883 | 853.0655 | 1134.3609 | 1410.3741 | 1800 | 804.6364 | 995.2431 | 1323.421 | 1645.4365 | 1149.4805 | 1421.7759 | 1890.6014 | 2350.6236 | 1800 | 1.28 | 1814.58 | 48.42 | 4.86 | 1.25 | 2220.54 | 64.8 | 4.86 | 1.28 | 2984.52 | 96.84 | 9.72 | 1.3 | 3737.28 | 129.6 | 9.72 | 1800 | 1.28 | 1779 | 1814.58 | 48.42 | 4.86 | 1800 | 1.25 | 2177 | 2220.54 | 64.8 | 4.86 | 1800 | 1.28 | 2926 | 2984.52 | 96.84 | 9.72 | 1800 | 1.3 | 3664 | 3737.28 | 129.6 | 9.72
1900 | 361.5145 | 446.8112 | 594.0275 | 733.8642 | 482.0194 | 595.7483 | 792.0367 | 978.4856 | 602.5242 | 744.6853 | 990.0458 | 1223.1069 | 723.0291 | 893.6224 | 1188.055 | 1467.7283 | 1900 | 843.5339 | 1042.5595 | 1386.0641 | 1712.3497 | 1205.0484 | 1489.3707 | 1980.0916 | 2446.2139 | 1900 | 1.28 | 1902.3 | 51.11 | 5.13 | 1.25 | 2326.11 | 68.4 | 5.13 | 1.28 | 3125.79 | 102.22 | 10.26 | 1.3 | 3889.26 | 136.8 | 10.26 | 1900 | 1.28 | 1865 | 1902.3 | 51.11 | 5.13 | 1900 | 1.25 | 2280.5 | 2326.11 | 68.4 | 5.13 | 1900 | 1.28 | 3064.5 | 3125.79 | 102.22 | 10.26 | 1900 | 1.3 | 3813 | 3889.26 | 136.8 | 10.26
2000 | 378.1849 | 467.0896 | 620.8745 | 762.5413 | 504.2465 | 622.7862 | 827.8327 | 1016.7217 | 630.3082 | 778.4827 | 1034.7909 | 1270.9021 | 756.3698 | 934.1793 | 1241.7491 | 1525.0825 | 2000 | 882.4314 | 1089.8758 | 1448.7073 | 1779.2629 | 1260.6163 | 1556.9654 | 2069.5818 | 2541.8042 | 2000 | 1.28 | 1990.02 | 53.8 | 5.4 | 1.25 | 2431.68 | 72 | 5.4 | 1.28 | 3267.06 | 107.6 | 10.8 | 1.3 | 4041.24 | 144 | 10.8 | 2000 | 1.28 | 1951 | 1990.02 | 53.8 | 5.4 | 2000 | 1.25 | 2384 | 2431.68 | 72 | 5.4 | 2000 | 1.28 | 3203 | 3267.06 | 107.6 | 10.8 | 2000 | 1.3 | 3962 | 4041.24 | 144 | 10.8
2100 | 394.6614 | 487.0742 | 647.4308 | 790.5447 | 526.2152 | 649.4322 | 863.2411 | 1054.0596 | 657.7691 | 811.7903 | 1079.0514 | 1317.5746 | 789.3229 | 974.1483 | 1294.8617 | 1581.0895 | 2100 | 920.8767 | 1136.5064 | 1510.672 | 1844.6044 | 1315.5381 | 1623.5806 | 2158.1028 | 2635.1491 | 2100 | 1.28 | 2076.72 | 56.49 | 5.67 | 1.25 | 2535.72 | 75.6 | 5.67 | 1.28 | 3406.8 | 112.98 | 11.34 | 1.3 | 4189.65 | 151.2 | 11.34 | 2100 | 1.28 | 2036 | 2076.72 | 56.49 | 5.67 | 2100 | 1.25 | 2486 | 2535.72 | 75.6 | 5.67 | 2100 | 1.28 | 3340 | 3406.8 | 112.98 | 11.34 | 2100 | 1.3 | 4107.5 | 4189.65 | 151.2 | 11.34
2200 | 409.6742 | 507.0587 | 673.9871 | 815.6339 | 546.2322 | 676.0783 | 898.6495 | 1087.5118 | 682.7903 | 845.0979 | 1123.3119 | 1359.3898 | 819.3483 | 1014.1174 | 1347.9743 | 1631.2677 | 2200 | 955.9064 | 1183.137 | 1572.6367 | 1903.1457 | 1365.5805 | 1690.1957 | 2246.6238 | 2718.7795 | 2200 | 1.29 | 2163.42 | 59.18 | 5.94 | 1.25 | 2639.76 | 79.2 | 5.94 | 1.28 | 3546.54 | 118.36 | 11.88 | 1.31 | 4338.06 | 158.4 | 11.88 | 2200 | 1.29 | 2121 | 2163.42 | 59.18 | 5.94 | 2200 | 1.25 | 2588 | 2639.76 | 79.2 | 5.94 | 2200 | 1.28 | 3477 | 3546.54 | 118.36 | 11.88 | 2200 | 1.31 | 4253 | 4338.06 | 158.4 | 11.88
2300 | 425.8989 | 526.7494 | 700.1557 | 842.9623 | 567.8652 | 702.3325 | 933.541 | 1123.9497 | 709.8315 | 877.9156 | 1166.9262 | 1404.9371 | 851.7977 | 1053.4987 | 1400.3115 | 1685.9246 | 2300 | 993.764 | 1229.0818 | 1633.6967 | 1966.912 | 1419.6629 | 1755.8312 | 2333.8525 | 2809.8743 | 2300 | 1.29 | 2249.1 | 61.87 | 6.21 | 1.25 | 2742.27 | 82.8 | 6.21 | 1.28 | 3684.24 | 123.74 | 12.42 | 1.31 | 4483.41 | 165.6 | 12.42 | 2300 | 1.29 | 2205 | 2249.1 | 61.87 | 6.21 | 2300 | 1.25 | 2688.5 | 2742.27 | 82.8 | 6.21 | 2300 | 1.28 | 3612 | 3684.24 | 123.74 | 12.42 | 2300 | 1.31 | 4395.5 | 4483.41 | 165.6 | 12.42
2400 | 440.5495 | 546.44 | 723.7384 | 870.2907 | 587.3993 | 728.5867 | 964.9845 | 1160.3876 | 734.2491 | 910.7334 | 1206.2306 | 1450.4845 | 881.0989 | 1092.88 | 1447.4767 | 1740.5814 | 2400 | 1027.9487 | 1275.0267 | 1688.7228 | 2030.6783 | 1468.4982 | 1821.4667 | 2412.4612 | 2900.9691 | 2400 | 1.3 | 2334.78 | 64.56 | 6.48 | 1.25 | 2844.78 | 86.4 | 6.48 | 1.29 | 3821.94 | 129.12 | 12.96 | 1.31 | 4628.76 | 172.8 | 12.96 | 2400 | 1.3 | 2289 | 2334.78 | 64.56 | 6.48 | 2400 | 1.25 | 2789 | 2844.78 | 86.4 | 6.48 | 2400 | 1.29 | 3747 | 3821.94 | 129.12 | 12.96 | 2400 | 1.31 | 4538 | 4628.76 | 172.8 | 12.96
2500 | 456.6202 | 565.8368 | 749.5241 | 896.9479 | 608.8269 | 754.449 | 999.3654 | 1195.9306 | 761.0336 | 943.0613 | 1249.2068 | 1494.9132 | 913.2404 | 1131.6735 | 1499.0481 | 1793.8958 | 2500 | 1065.4471 | 1320.2858 | 1748.8895 | 2092.8785 | 1522.0673 | 1886.1226 | 2498.4136 | 2989.8264 | 2500 | 1.3 | 2419.95 | 67.25 | 6.75 | 1.25 | 2945.76 | 90 | 6.75 | 1.29 | 3958.11 | 134.5 | 13.5 | 1.31 | 4770.54 | 180 | 13.5 | 2500 | 1.3 | 2372.5 | 2419.95 | 67.25 | 6.75 | 2500 | 1.25 | 2888 | 2945.76 | 90 | 6.75 | 2500 | 1.29 | 3880.5 | 3958.11 | 134.5 | 13.5 | 2500 | 1.31 | 4677 | 4770.54 | 180 | 13.5
2600 | [16 empty] | 2600 | [9 empty] | 1.3 | 2505.12 | 69.94 | 7.02 | 1.25 | 3046.74 | 93.6 | 7.02 | 1.29 | 4094.28 | 139.88 | 14.04 | 1.32 | 4912.32 | 187.2 | 14.04 | 2600 | 1.3 | 2456 | 2505.12 | 69.94 | 7.02 | 2600 | 1.25 | 2987 | 3046.74 | 93.6 | 7.02 | 2600 | 1.29 | 4014 | 4094.28 | 139.88 | 14.04 | 2600 | 1.32 | 4816 | 4912.32 | 187.2 | 14.04
2700 | [16 empty] | 2700 | [9 empty] | 1.3 | 2589.27 | 72.63 | 7.29 | 1.25 | 3147.21 | 97.2 | 7.29 | 1.29 | 4228.92 | 145.26 | 14.58 | 1.32 | 5051.55 | 194.4 | 14.58 | 2700 | 1.3 | 2538.5 | 2589.27 | 72.63 | 7.29 | 2700 | 1.25 | 3085.5 | 3147.21 | 97.2 | 7.29 | 2700 | 1.29 | 4146 | 4228.92 | 145.26 | 14.58 | 2700 | 1.32 | 4952.5 | 5051.55 | 194.4 | 14.58
2800 | [16 empty] | 2800 | [9 empty] | 1.31 | 2673.42 | 75.32 | 7.56 | 1.25 | 3247.68 | 100.8 | 7.56 | 1.3 | 4363.56 | 150.64 | 15.12 | 1.32 | 5190.78 | 201.6 | 15.12 | 2800 | 1.31 | 2621 | 2673.42 | 75.32 | 7.56 | 2800 | 1.25 | 3184 | 3247.68 | 100.8 | 7.56 | 2800 | 1.3 | 4278 | 4363.56 | 150.64 | 15.12 | 2800 | 1.32 | 5089 | 5190.78 | 201.6 | 15.12
2900 | [16 empty] | 2900 | [9 empty] | 1.31 | 2756.55 | 78.01 | 7.83 | 1.25 | 3347.13 | 104.4 | 7.83 | 1.3 | 4496.67 | 156.02 | 15.66 | 1.32 | 5327.46 | 208.8 | 15.66 | 2900 | 1.31 | 2702.5 | 2756.55 | 78.01 | 7.83 | 2900 | 1.25 | 3281.5 | 3347.13 | 104.4 | 7.83 | 2900 | 1.3 | 4408.5 | 4496.67 | 156.02 | 15.66 | 2900 | 1.32 | 5223 | 5327.46 | 208.8 | 15.66
3000 | [16 empty] | 3000 | [9 empty] | 1.31 | 2839.68 | 80.7 | 8.1 | 1.25 | 3446.58 | 108 | 8.1 | 1.3 | 4629.78 | 161.4 | 16.2 | 1.33 | 5464.14 | 216 | 16.2 | 3000 | 1.31 | 2784 | 2839.68 | 80.7 | 8.1 | 3000 | 1.25 | 3379 | 3446.58 | 108 | 8.1 | 3000 | 1.3 | 4539 | 4629.78 | 161.4 | 16.2 | 3000 | 1.33 | 5357 | 5464.14 | 216 | 16.2
3100 | [16 empty] | 3100 | [9 empty] | 1.31 | 2922.3 | 83.39 | 8.37 | 1.25 | 3545.01 | 111.6 | 8.37 | 1.3 | 4761.87 | 166.78 | 16.74 | 1.33 | 5598.27 | 223.2 | 16.74 | 3100 | 1.31 | 2865 | 2922.3 | 83.39 | 8.37 | 3100 | 1.25 | 3475.5 | 3545.01 | 111.6 | 8.37 | 3100 | 1.3 | 4668.5 | 4761.87 | 166.78 | 16.74 | 3100 | 1.33 | 5488.5 | 5598.27 | 223.2 | 16.74
3200 | [16 empty] | 3200 | [9 empty] | 1.32 | 3004.92 | 86.08 | 8.64 | 1.25 | 3643.44 | 115.2 | 8.64 | 1.3 | 4893.96 | 172.16 | 17.28 | 1.34 | 5732.4 | 230.4 | 17.28 | 3200 | 1.32 | 2946 | 3004.92 | 86.08 | 8.64 | 3200 | 1.25 | 3572 | 3643.44 | 115.2 | 8.64 | 3200 | 1.3 | 4798 | 4893.96 | 172.16 | 17.28 | 3200 | 1.34 | 5620 | 5732.4 | 230.4 | 17.28
3300 | [16 empty] | 3300 | [9 empty] | 1.32 | 3087.03 | 88.77 | 8.91 | 1.25 | 3740.85 | 118.8 | 8.91 | 1.3 | 5024.52 | 177.54 | 17.82 | 1.34 | 5865 | 237.6 | 17.82 | 3300 | 1.32 | 3026.5 | 3087.03 | 88.77 | 8.91 | 3300 | 1.25 | 3667.5 | 3740.85 | 118.8 | 8.91 | 3300 | 1.3 | 4926 | 5024.52 | 177.54 | 17.82 | 3300 | 1.34 | 5750 | 5865 | 237.6 | 17.82
3400 | [16 empty] | 3400 | [9 empty] | 1.32 | 3169.14 | 91.46 | 9.18 | 1.25 | 3838.26 | 122.4 | 9.18 | 1.31 | 5155.08 | 182.92 | 18.36 | 1.34 | 5997.6 | 244.8 | 18.36 | 3400 | 1.32 | 3107 | 3169.14 | 91.46 | 9.18 | 3400 | 1.25 | 3763 | 3838.26 | 122.4 | 9.18 | 3400 | 1.31 | 5054 | 5155.08 | 182.92 | 18.36 | 3400 | 1.34 | 5880 | 5997.6 | 244.8 | 18.36
3500 | [16 empty] | 3500 | [9 empty] | 1.32 | 3250.74 | 94.15 | 9.45 | 1.25 | 3934.65 | 126 | 9.45 | 1.31 | 5285.13 | 188.3 | 18.9 | 1.34 | 6127.65 | 252 | 18.9 | 3500 | 1.32 | 3187 | 3250.74 | 94.15 | 9.45 | 3500 | 1.25 | 3857.5 | 3934.65 | 126 | 9.45 | 3500 | 1.31 | 5181.5 | 5285.13 | 188.3 | 18.9 | 3500 | 1.34 | 6007.5 | 6127.65 | 252 | 18.9
3600 | [16 empty] | 3600 | [9 empty] | 1.33 | 3332.34 | 96.84 | 9.72 | 1.25 | 4031.04 | 129.6 | 9.72 | 1.31 | 5415.18 | 193.68 | 19.44 | 1.35 | 6257.7 | 259.2 | 19.44 | 3600 | 1.33 | 3267 | 3332.34 | 96.84 | 9.72 | 3600 | 1.25 | 3952 | 4031.04 | 129.6 | 9.72 | 3600 | 1.31 | 5309 | 5415.18 | 193.68 | 19.44 | 3600 | 1.35 | 6135 | 6257.7 | 259.2 | 19.44
3700 | [16 empty] | 3700 | [9 empty] | 1.33 | 3412.92 | 99.53 | 9.99 | 1.25 | 4126.92 | 133.2 | 9.99 | 1.31 | 5544.21 | 199.06 | 19.98 | 1.35 | 6386.22 | 266.4 | 19.98 | 3700 | 1.33 | 3346 | 3412.92 | 99.53 | 9.99 | 3700 | 1.25 | 4046 | 4126.92 | 133.2 | 9.99 | 3700 | 1.31 | 5435.5 | 5544.21 | 199.06 | 19.98 | 3700 | 1.35 | 6261 | 6386.22 | 266.4 | 19.98
3800 | [16 empty] | 3800 | [9 empty] | 1.34 | 3493.5 | 102.22 | 10.26 | 1.25 | 4222.8 | 136.8 | 10.26 | 1.32 | 5673.24 | 204.44 | 20.52 | 1.35 | 6514.74 | 273.6 | 20.52 | 3800 | 1.34 | 3425 | 3493.5 | 102.22 | 10.26 | 3800 | 1.25 | 4140 | 4222.8 | 136.8 | 10.26 | 3800 | 1.32 | 5562 | 5673.24 | 204.44 | 20.52 | 3800 | 1.35 | 6387 | 6514.74 | 273.6 | 20.52
3900 | [16 empty] | 3900 | [9 empty] | 1.34 | 3574.08 | 104.91 | 10.53 | 1.25 | 4318.17 | 140.4 | 10.53 | 1.32 | 5800.74 | 209.82 | 21.06 | 1.35 | 6641.22 | 280.8 | 21.06 | 3900 | 1.34 | 3504 | 3574.08 | 104.91 | 10.53 | 3900 | 1.25 | 4233.5 | 4318.17 | 140.4 | 10.53 | 3900 | 1.32 | 5687 | 5800.74 | 209.82 | 21.06 | 3900 | 1.35 | 6511 | 6641.22 | 280.8 | 21.06
4000 | [16 empty] | 4000 | [9 empty] | 1.34 | 3654.66 | 107.6 | 10.8 | 1.25 | 4413.54 | 144 | 10.8 | 1.32 | 5928.24 | 215.2 | 21.6 | 1.36 | 6767.7 | 288 | 21.6 | 4000 | 1.34 | 3583 | 3654.66 | 107.6 | 10.8 | 4000 | 1.25 | 4327 | 4413.54 | 144 | 10.8 | 4000 | 1.32 | 5812 | 5928.24 | 215.2 | 21.6 | 4000 | 1.36 | 6635 | 6767.7 | 288 | 21.6
Height [mm] | Single |  | Double |  | Single |  | Double |  | Single |  | Double |  | Single |  | Double |  | Height [mm] | Single |  | Double |  | Single |  | Double |  | Height [mm] | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m
Type | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | Type | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D
Length [mm] | 300 |  |  |  | 400 |  |  |  | 500 |  |  |  | 600 |  |  |  | Length [mm] | 700 | 600 |  |  | 1000 | 0
*The reduction factor is used for heat output reduction, e.g. when radiators are to be installed in trenches or under ceilings
Revised: | 2013-12-10 09:29
Print

## Flow (l-h)
|  |  | Hudevad |  |  |  | Temperature set
Saltgade 11
|  |  | DK-6760 Ribe |  |  |  | Flow temperature |  |  | Return temperature |  |  | Room temperature |  |  | ∆T
|  |  | 0 |  |  |  | Tf |  |  | Tr |  |  | Ti |  |  | dTln
[7 empty] | 70 |  |  | 40 |  |  | 20 |  |  | 35
www.hudevad.com
[7 empty] | Reduction factor * [%] |  |  | 0%
Temperature set | P5V/P5KV/P5V-D/P5KV-D | 0 | [14 empty] | Temperature set | P5V/P5KV/P5V-D/P5KV-D | [7 empty] | RADIATOR DATA
70/40-20 | [16 empty] | 70/40-20 | [49 empty] | /
-
Length [mm] | 300 |  |  |  | 400 |  |  |  | 500 |  |  |  | 600 |  |  |  | Length [mm] | 700 | 600 |  |  | 1000 |  | 700 |  |  | P5V |  |  |  | P5KV |  |  |  | P5V-D |  |  |  | P5KV-D |  |  |  | P5V | [5 empty] | P5KV | [5 empty] | P5V-D | [5 empty] | P5KV-D
Type | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | Type | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | Height [mm] | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m
Height [mm] | Enkelt |  | Dobbelt |  | Enkelt |  | Dobbelt |  | Enkelt |  | Dobbelt |  | Enkelt |  | Dobbelt |  | Height [mm] | Enkelt | Enkelt | Dobbelt | #REF! | Enkelt | Enkelt | Dobbelt | #REF! | [17 empty] | Height [mm] | n | W/m (75/65-20) | Tillæg | KG/m | L/m | Height [mm] | n | W/m (75/65-20) | Tillæg | KG/m | L/m | Height [mm] | n | W/m (75/65-20) | Tillæg | KG/m | L/m | Height [mm] | n | W/m (75/65-20) | Tillæg | KG/m | L/m |  | Stamdata
800 | 4.908 | 6.0873 | 8.1527 | 11.1736 | 6.544 | 8.1164 | 10.8703 | 14.8981 | 8.18 | 10.1454 | 13.5879 | 18.6226 | 9.816 | 12.1745 | 16.3055 | 22.3472 | 800 | 11.452 | 14.2036 | 19.0231 | 26.0717 | 16.36 | 20.2909 | 27.1758 | 37.2453 | 800 | 1.25 | 891.48 | 21.52 | 2.16 | 1.25 | 1105.68 | 28.8 | 2.16 | 1.26 | 1486.14 | 43.04 | 4.32 | 1.27 | 2044.08 | 57.6 | 0 | 800 | 1.25 | 874 | 891.48 | 21.52 | 2.16 | 800 | 1.25 | 1084 | 1105.68 | 28.8 | 2.16 | 800 | 1.26 | 1457 | 1486.14 | 43.04 | 4.32 | 800 | 1.27 | 2004 | 2044.08 | 57.6 | 4.32
900 | 5.4387 | 6.7302 | 9.0145 | 12.1828 | 7.2516 | 8.9737 | 12.0193 | 16.2437 | 9.0644 | 11.2171 | 15.0241 | 20.3046 | 10.8773 | 13.4605 | 18.0289 | 24.3656 | 900 | 12.6902 | 15.7039 | 21.0337 | 28.4265 | 18.1289 | 22.4342 | 30.0482 | 40.6093 | 900 | 1.25 | 987.87 | 24.21 | 2.43 | 1.25 | 1222.47 | 32.4 | 2.43 | 1.26 | 1643.22 | 48.42 | 4.86 | 1.27 | 2228.7 | 64.8 | 4.86 | 900 | 1.25 | 968.5 | 987.87 | 24.21 | 2.43 | 900 | 1.25 | 1198.5 | 1222.47 | 32.4 | 2.43 | 900 | 1.26 | 1611 | 1643.22 | 48.42 | 4.86 | 900 | 1.27 | 2185 | 2228.7 | 64.8 | 4.86 |  | 1 | [11 empty] | Produkt type
1000 | 5.9693 | 7.3732 | 9.8762 | 13.145 | 7.9591 | 9.831 | 13.1682 | 17.5267 | 9.9489 | 12.2887 | 16.4603 | 21.9083 | 11.9387 | 14.7465 | 19.7523 | 26.29 | 1000 | 13.9285 | 17.2042 | 23.0444 | 30.6717 | 19.8978 | 24.5774 | 32.9206 | 43.8167 | 1000 | 1.25 | 1084.26 | 26.9 | 2.7 | 1.25 | 1339.26 | 36 | 2.7 | 1.26 | 1800.3 | 53.8 | 5.4 | 1.28 | 2413.32 | 72 | 5.4 | 1000 | 1.25 | 1063 | 1084.26 | 26.9 | 2.7 | 1000 | 1.25 | 1313 | 1339.26 | 36 | 2.7 | 1000 | 1.26 | 1765 | 1800.3 | 53.8 | 5.4 | 1000 | 1.28 | 2366 | 2413.32 | 72 | 5.4 |  | language | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
1100 | 6.486 | 7.9994 | 10.7155 | 14.1006 | 8.648 | 10.6658 | 14.2873 | 18.8008 | 10.81 | 13.3323 | 17.8592 | 23.501 | 12.9719 | 15.9987 | 21.431 | 28.2012 | 1100 | 15.1339 | 18.6652 | 25.0029 | 32.9014 | 21.6199 | 26.6645 | 35.7184 | 47.002 | 1100 | 1.25 | 1178.1 | 29.59 | 2.97 | 1.25 | 1452.99 | 39.6 | 2.97 | 1.26 | 1953.3 | 59.18 | 5.94 | 1.28 | 2588.76 | 79.2 | 5.94 | 1100 | 1.25 | 1155 | 1178.1 | 29.59 | 2.97 | 1100 | 1.25 | 1424.5 | 1452.99 | 39.6 | 2.97 | 1100 | 1.26 | 1915 | 1953.3 | 59.18 | 5.94 | 1100 | 1.28 | 2538 | 2588.76 | 79.2 | 5.94 |  | Dansk | 1 | Saltgade 11 | DK-6760 Ribe | Tel.: +45 7542 0255 | www.rio.dk | www.hudevad.dk | Indtast temperatursæt | Fremløbstemperatur | Returtemperatur | Rumtemperatur | Reduceringsfaktor * [%] | P5 / P5K + P5-D / P5K-D | Højde [mm] | Dybde [mm] | Længde [mm] | Temperatursæt | *Reduceringsfaktor anvendes ved reduktion af varmeydelsen, f.eks. hvor radiatorer skal monteres i grav eller under loft | Enkelt | Dobbelt | RADIATOR DATA
1200 | 6.9777 | 8.6255 | 11.5137 | 15.0562 | 9.3036 | 11.5007 | 15.3516 | 20.0749 | 11.6295 | 14.3758 | 19.1895 | 25.0937 | 13.9553 | 17.251 | 23.0274 | 30.1124 | 1200 | 16.2812 | 20.1262 | 26.8653 | 35.1311 | 23.2589 | 28.7517 | 38.379 | 50.1873 | 1200 | 1.26 | 1271.94 | 32.28 | 3.24 | 1.25 | 1566.72 | 43.2 | 3.24 | 1.27 | 2106.3 | 64.56 | 6.48 | 1.28 | 2764.2 | 86.4 | 6.48 | 1200 | 1.26 | 1247 | 1271.94 | 32.28 | 3.24 | 1200 | 1.25 | 1536 | 1566.72 | 43.2 | 3.24 | 1200 | 1.27 | 2065 | 2106.3 | 64.56 | 6.48 | 1200 | 1.28 | 2710 | 2764.2 | 86.4 | 6.48 |  | Deutsch | 2 | Saltgade 11 | DK-6760 Ribe | Tel.: +45 7542 0255 | www.riopanel.de | www.hudevad.de | Temperatursatz eingeben | Vorlauftemperatur | Rücklauftemperatur | Raumtemperatur | Reduktionsfaktor * [%] | P5 / P5K + P5-D / P5K-D | Bauhöhe [mm] | Bautiefen [mm] | Baulänge [mm] | Temperatursatz | *Der Reduktionsfaktor wird für die Reduzierung der Wärmeleistung verwendet, z.B. wenn Heizkörper in Gräben oder unter Decken zu montieren sind | Einlagig | Doppellagig | HEIZKÖRPER DATEN
1300 | 7.4813 | 9.2376 | 12.3277 | 15.9701 | 9.975 | 12.3168 | 16.437 | 21.2935 | 12.4688 | 15.396 | 20.5462 | 26.6169 | 14.9625 | 18.4752 | 24.6555 | 31.9402 | 1300 | 17.4563 | 21.5544 | 28.7647 | 37.2636 | 24.9376 | 30.792 | 41.0925 | 53.2337 | 1300 | 1.26 | 1363.74 | 34.97 | 3.51 | 1.25 | 1677.9 | 46.8 | 3.51 | 1.27 | 2255.22 | 69.94 | 7.02 | 1.28 | 2931.99 | 93.6 | 7.02 | 1300 | 1.26 | 1337 | 1363.74 | 34.97 | 3.51 | 1300 | 1.25 | 1645 | 1677.9 | 46.8 | 3.51 | 1300 | 1.27 | 2211 | 2255.22 | 69.94 | 7.02 | 1300 | 1.28 | 2874.5 | 2931.99 | 93.6 | 7.02 |  | English | 3 | Unit 5 Cyan Park - Phoenix Way | Coventry, CV2 4QP | Tel.: +44 (0) 2476 88 1200 | www.riopanel.com | www.hudevad.com | Enter temperature set | Flow temperature | Return temperature | Room temperature | Reduction factor * [%] | P5 / P5K + P5-D / P5K-D | Height [mm] | Depth [mm] | Length [mm] | Temperature set | *The reduction factor is used for heat output reduction, e.g. when radiators are to be installed in trenches or under ceilings | Single | Double | RADIATOR DATA
1400 | 7.9564 | 9.8497 | 13.1418 | 16.8239 | 10.6086 | 13.1329 | 17.5224 | 22.4319 | 13.2607 | 16.4162 | 21.903 | 28.0399 | 15.9129 | 19.6994 | 26.2836 | 33.6479 | 1400 | 18.565 | 22.9826 | 30.6642 | 39.2559 | 26.5215 | 32.8323 | 43.806 | 56.0798 | 1400 | 1.27 | 1455.54 | 37.66 | 3.78 | 1.25 | 1789.08 | 50.4 | 3.78 | 1.27 | 2404.14 | 75.32 | 7.56 | 1.29 | 3099.78 | 100.8 | 7.56 | 1400 | 1.27 | 1427 | 1455.54 | 37.66 | 3.78 | 1400 | 1.25 | 1754 | 1789.08 | 50.4 | 3.78 | 1400 | 1.27 | 2357 | 2404.14 | 75.32 | 7.56 | 1400 | 1.29 | 3039 | 3099.78 | 100.8 | 7.56 |  | François | 4 | Plomb'Art | Kim Staeger-Holst | Tel.: +33 180 815310 | www.riopanel.com | www.hudevad.com
1500 | 8.4527 | 10.4506 | 13.9419 | 17.7014 | 11.2702 | 13.9341 | 18.5892 | 23.6019 | 14.0878 | 17.4176 | 23.2365 | 29.5023 | 16.9053 | 20.9011 | 27.8838 | 35.4028 | 1500 | 19.7229 | 24.3846 | 32.5311 | 41.3033 | 28.1756 | 34.8352 | 46.473 | 59.0046 | 1500 | 1.27 | 1546.32 | 40.35 | 4.05 | 1.25 | 1898.22 | 54 | 4.05 | 1.27 | 2550.51 | 80.7 | 8.1 | 1.29 | 3261.45 | 108 | 8.1 | 1500 | 1.27 | 1516 | 1546.32 | 40.35 | 4.05 | 1500 | 1.25 | 1861 | 1898.22 | 54 | 4.05 | 1500 | 1.27 | 2500.5 | 2550.51 | 80.7 | 8.1 | 1500 | 1.29 | 3197.5 | 3261.45 | 108 | 8.1 |  | Norsk | 5 | Saltgade 11 | DK-6760 Ribe | Tel.: +45 7542 0255 | www.riopanel.com | www.hudevad.com
1600 | 8.9489 | 11.0514 | 14.742 | 18.5789 | 11.9319 | 14.7352 | 19.656 | 24.7718 | 14.9148 | 18.419 | 24.57 | 30.9648 | 17.8978 | 22.1028 | 29.484 | 37.1577 | 1600 | 20.8808 | 25.7866 | 34.398 | 43.3507 | 29.8297 | 36.8381 | 49.14 | 61.9295 | 1600 | 1.27 | 1637.1 | 43.04 | 4.32 | 1.25 | 2007.36 | 57.6 | 4.32 | 1.27 | 2696.88 | 86.08 | 8.64 | 1.29 | 3423.12 | 115.2 | 8.64 | 1600 | 1.27 | 1605 | 1637.1 | 43.04 | 4.32 | 1600 | 1.25 | 1968 | 2007.36 | 57.6 | 4.32 | 1600 | 1.27 | 2644 | 2696.88 | 86.08 | 8.64 | 1600 | 1.29 | 3356 | 3423.12 | 115.2 | 8.64 |  | Svenska | 6 | Saltgade 11 | DK-6760 Ribe | Tel.: +45 7542 0255 | www.riopanel.com | www.hudevad.com
1700 | 9.434 | 11.6382 | 15.5282 | 19.4314 | 12.5787 | 15.5177 | 20.7042 | 25.9085 | 15.7233 | 19.3971 | 25.8803 | 32.3857 | 18.868 | 23.2765 | 31.0563 | 38.8628 | 1700 | 22.0126 | 27.1559 | 36.2324 | 45.3399 | 31.4466 | 38.7942 | 51.7606 | 64.7713 | 1700 | 1.27 | 1725.84 | 45.73 | 4.59 | 1.25 | 2113.95 | 61.2 | 4.59 | 1.27 | 2840.7 | 91.46 | 9.18 | 1.29 | 3580.2 | 122.4 | 9.18 | 1700 | 1.27 | 1692 | 1725.84 | 45.73 | 4.59 | 1700 | 1.25 | 2072.5 | 2113.95 | 61.2 | 4.59 | 1700 | 1.27 | 2785 | 2840.7 | 91.46 | 9.18 | 1700 | 1.29 | 3510 | 3580.2 | 122.4 | 9.18
1800 | 9.8838 | 12.2251 | 16.2562 | 20.2117 | 13.1783 | 16.3001 | 21.675 | 26.949 | 16.4729 | 20.3751 | 27.0937 | 33.6862 | 19.7675 | 24.4501 | 32.5125 | 40.4234 | 1800 | 23.0621 | 28.5252 | 37.9312 | 47.1607 | 32.9458 | 40.7502 | 54.1875 | 67.3724 | 1800 | 1.28 | 1814.58 | 48.42 | 4.86 | 1.25 | 2220.54 | 64.8 | 4.86 | 1.28 | 2984.52 | 96.84 | 9.72 | 1.3 | 3737.28 | 129.6 | 9.72 | 1800 | 1.28 | 1779 | 1814.58 | 48.42 | 4.86 | 1800 | 1.25 | 2177 | 2220.54 | 64.8 | 4.86 | 1800 | 1.28 | 2926 | 2984.52 | 96.84 | 9.72 | 1800 | 1.3 | 3664 | 3737.28 | 129.6 | 9.72
1900 | 10.3616 | 12.8063 | 17.0257 | 21.0337 | 13.8154 | 17.075 | 22.701 | 28.0449 | 17.2693 | 21.3438 | 28.3762 | 35.0561 | 20.7231 | 25.6126 | 34.0514 | 42.0673 | 1900 | 24.177 | 29.8813 | 39.7267 | 49.0785 | 34.5385 | 42.6876 | 56.7524 | 70.1122 | 1900 | 1.28 | 1902.3 | 51.11 | 5.13 | 1.25 | 2326.11 | 68.4 | 5.13 | 1.28 | 3125.79 | 102.22 | 10.26 | 1.3 | 3889.26 | 136.8 | 10.26 | 1900 | 1.28 | 1865 | 1902.3 | 51.11 | 5.13 | 1900 | 1.25 | 2280.5 | 2326.11 | 68.4 | 5.13 | 1900 | 1.28 | 3064.5 | 3125.79 | 102.22 | 10.26 | 1900 | 1.3 | 3813 | 3889.26 | 136.8 | 10.26
2000 | 10.8393 | 13.3875 | 17.7952 | 21.8556 | 14.4525 | 17.85 | 23.7269 | 29.1408 | 18.0656 | 22.3125 | 29.6587 | 36.426 | 21.6787 | 26.775 | 35.5904 | 43.7112 | 2000 | 25.2918 | 31.2375 | 41.5221 | 50.9964 | 36.1312 | 44.625 | 59.3173 | 72.8519 | 2000 | 1.28 | 1990.02 | 53.8 | 5.4 | 1.25 | 2431.68 | 72 | 5.4 | 1.28 | 3267.06 | 107.6 | 10.8 | 1.3 | 4041.24 | 144 | 10.8 | 2000 | 1.28 | 1951 | 1990.02 | 53.8 | 5.4 | 2000 | 1.25 | 2384 | 2431.68 | 72 | 5.4 | 2000 | 1.28 | 3203 | 3267.06 | 107.6 | 10.8 | 2000 | 1.3 | 3962 | 4041.24 | 144 | 10.8
2100 | 11.3116 | 13.9603 | 18.5563 | 22.6582 | 15.0821 | 18.6137 | 24.7418 | 30.2109 | 18.8527 | 23.2671 | 30.9272 | 37.7637 | 22.6232 | 27.9206 | 37.1127 | 45.3164 | 2100 | 26.3937 | 32.574 | 43.2981 | 52.8691 | 37.7053 | 46.5343 | 61.8545 | 75.5273 | 2100 | 1.28 | 2076.72 | 56.49 | 5.67 | 1.25 | 2535.72 | 75.6 | 5.67 | 1.28 | 3406.8 | 112.98 | 11.34 | 1.3 | 4189.65 | 151.2 | 11.34 | 2100 | 1.28 | 2036 | 2076.72 | 56.49 | 5.67 | 2100 | 1.25 | 2486 | 2535.72 | 75.6 | 5.67 | 2100 | 1.28 | 3340 | 3406.8 | 112.98 | 11.34 | 2100 | 1.3 | 4107.5 | 4189.65 | 151.2 | 11.34
2200 | 11.7419 | 14.5331 | 19.3175 | 23.3773 | 15.6558 | 19.3774 | 25.7566 | 31.1697 | 19.5698 | 24.2218 | 32.1958 | 38.9622 | 23.4838 | 29.0661 | 38.635 | 46.7546 | 2200 | 27.3977 | 33.9105 | 45.0741 | 54.547 | 39.1396 | 48.4436 | 64.3916 | 77.9243 | 2200 | 1.29 | 2163.42 | 59.18 | 5.94 | 1.25 | 2639.76 | 79.2 | 5.94 | 1.28 | 3546.54 | 118.36 | 11.88 | 1.31 | 4338.06 | 158.4 | 11.88 | 2200 | 1.29 | 2121 | 2163.42 | 59.18 | 5.94 | 2200 | 1.25 | 2588 | 2639.76 | 79.2 | 5.94 | 2200 | 1.28 | 3477 | 3546.54 | 118.36 | 11.88 | 2200 | 1.31 | 4253 | 4338.06 | 158.4 | 11.88
2300 | 12.2069 | 15.0974 | 20.0675 | 24.1606 | 16.2759 | 20.1299 | 26.7567 | 32.2141 | 20.3448 | 25.1624 | 33.4459 | 40.2676 | 24.4138 | 30.1949 | 40.135 | 48.3211 | 2300 | 28.4828 | 35.2273 | 46.8242 | 56.3747 | 40.6897 | 50.3248 | 66.8917 | 80.5352 | 2300 | 1.29 | 2249.1 | 61.87 | 6.21 | 1.25 | 2742.27 | 82.8 | 6.21 | 1.28 | 3684.24 | 123.74 | 12.42 | 1.31 | 4483.41 | 165.6 | 12.42 | 2300 | 1.29 | 2205 | 2249.1 | 61.87 | 6.21 | 2300 | 1.25 | 2688.5 | 2742.27 | 82.8 | 6.21 | 2300 | 1.28 | 3612 | 3684.24 | 123.74 | 12.42 | 2300 | 1.31 | 4395.5 | 4483.41 | 165.6 | 12.42
2400 | 12.6268 | 15.6618 | 20.7434 | 24.9438 | 16.8357 | 20.8824 | 27.6579 | 33.2585 | 21.0447 | 26.103 | 34.5724 | 41.5731 | 25.2536 | 31.3236 | 41.4869 | 49.8877 | 2400 | 29.4626 | 36.5442 | 48.4013 | 58.2023 | 42.0894 | 52.206 | 69.1448 | 83.1461 | 2400 | 1.3 | 2334.78 | 64.56 | 6.48 | 1.25 | 2844.78 | 86.4 | 6.48 | 1.29 | 3821.94 | 129.12 | 12.96 | 1.31 | 4628.76 | 172.8 | 12.96 | 2400 | 1.3 | 2289 | 2334.78 | 64.56 | 6.48 | 2400 | 1.25 | 2789 | 2844.78 | 86.4 | 6.48 | 2400 | 1.29 | 3747 | 3821.94 | 129.12 | 12.96 | 2400 | 1.31 | 4538 | 4628.76 | 172.8 | 12.96
2500 | 13.0874 | 16.2177 | 21.4825 | 25.7079 | 17.4499 | 21.6236 | 28.6433 | 34.2772 | 21.8124 | 27.0296 | 35.8041 | 42.8465 | 26.1748 | 32.4355 | 42.965 | 51.4158 | 2500 | 30.5373 | 37.8414 | 50.1258 | 59.9851 | 43.6247 | 54.0591 | 71.6083 | 85.6929 | 2500 | 1.3 | 2419.95 | 67.25 | 6.75 | 1.25 | 2945.76 | 90 | 6.75 | 1.29 | 3958.11 | 134.5 | 13.5 | 1.31 | 4770.54 | 180 | 13.5 | 2500 | 1.3 | 2372.5 | 2419.95 | 67.25 | 6.75 | 2500 | 1.25 | 2888 | 2945.76 | 90 | 6.75 | 2500 | 1.29 | 3880.5 | 3958.11 | 134.5 | 13.5 | 2500 | 1.31 | 4677 | 4770.54 | 180 | 13.5
2600 | [16 empty] | 2600 | [8 empty] | 2600 | 1.3 | 2505.12 | 69.94 | 7.02 | 1.25 | 3046.74 | 93.6 | 7.02 | 1.29 | 4094.28 | 139.88 | 14.04 | 1.32 | 4912.32 | 187.2 | 14.04 | 2600 | 1.3 | 2456 | 2505.12 | 69.94 | 7.02 | 2600 | 1.25 | 2987 | 3046.74 | 93.6 | 7.02 | 2600 | 1.29 | 4014 | 4094.28 | 139.88 | 14.04 | 2600 | 1.32 | 4816 | 4912.32 | 187.2 | 14.04
2700 | [16 empty] | 2700 | [8 empty] | 2700 | 1.3 | 2589.27 | 72.63 | 7.29 | 1.25 | 3147.21 | 97.2 | 7.29 | 1.29 | 4228.92 | 145.26 | 14.58 | 1.32 | 5051.55 | 194.4 | 14.58 | 2700 | 1.3 | 2538.5 | 2589.27 | 72.63 | 7.29 | 2700 | 1.25 | 3085.5 | 3147.21 | 97.2 | 7.29 | 2700 | 1.29 | 4146 | 4228.92 | 145.26 | 14.58 | 2700 | 1.32 | 4952.5 | 5051.55 | 194.4 | 14.58
2800 | [16 empty] | 2800 | [8 empty] | 2800 | 1.31 | 2673.42 | 75.32 | 7.56 | 1.25 | 3247.68 | 100.8 | 7.56 | 1.3 | 4363.56 | 150.64 | 15.12 | 1.32 | 5190.78 | 201.6 | 15.12 | 2800 | 1.31 | 2621 | 2673.42 | 75.32 | 7.56 | 2800 | 1.25 | 3184 | 3247.68 | 100.8 | 7.56 | 2800 | 1.3 | 4278 | 4363.56 | 150.64 | 15.12 | 2800 | 1.32 | 5089 | 5190.78 | 201.6 | 15.12
2900 | [16 empty] | 2900 | [8 empty] | 2900 | 1.31 | 2756.55 | 78.01 | 7.83 | 1.25 | 3347.13 | 104.4 | 7.83 | 1.3 | 4496.67 | 156.02 | 15.66 | 1.32 | 5327.46 | 208.8 | 15.66 | 2900 | 1.31 | 2702.5 | 2756.55 | 78.01 | 7.83 | 2900 | 1.25 | 3281.5 | 3347.13 | 104.4 | 7.83 | 2900 | 1.3 | 4408.5 | 4496.67 | 156.02 | 15.66 | 2900 | 1.32 | 5223 | 5327.46 | 208.8 | 15.66
3000 | [16 empty] | 3000 | [8 empty] | 3000 | 1.31 | 2839.68 | 80.7 | 8.1 | 1.25 | 3446.58 | 108 | 8.1 | 1.3 | 4629.78 | 161.4 | 16.2 | 1.33 | 5464.14 | 216 | 16.2 | 3000 | 1.31 | 2784 | 2839.68 | 80.7 | 8.1 | 3000 | 1.25 | 3379 | 3446.58 | 108 | 8.1 | 3000 | 1.3 | 4539 | 4629.78 | 161.4 | 16.2 | 3000 | 1.33 | 5357 | 5464.14 | 216 | 16.2
3100 | [16 empty] | 3100 | [8 empty] | 3100 | 1.31 | 2922.3 | 83.39 | 8.37 | 1.25 | 3545.01 | 111.6 | 8.37 | 1.3 | 4761.87 | 166.78 | 16.74 | 1.33 | 5598.27 | 223.2 | 16.74 | 3100 | 1.31 | 2865 | 2922.3 | 83.39 | 8.37 | 3100 | 1.25 | 3475.5 | 3545.01 | 111.6 | 8.37 | 3100 | 1.3 | 4668.5 | 4761.87 | 166.78 | 16.74 | 3100 | 1.33 | 5488.5 | 5598.27 | 223.2 | 16.74
3200 | [16 empty] | 3200 | [8 empty] | 3200 | 1.32 | 3004.92 | 86.08 | 8.64 | 1.25 | 3643.44 | 115.2 | 8.64 | 1.3 | 4893.96 | 172.16 | 17.28 | 1.34 | 5732.4 | 230.4 | 17.28 | 3200 | 1.32 | 2946 | 3004.92 | 86.08 | 8.64 | 3200 | 1.25 | 3572 | 3643.44 | 115.2 | 8.64 | 3200 | 1.3 | 4798 | 4893.96 | 172.16 | 17.28 | 3200 | 1.34 | 5620 | 5732.4 | 230.4 | 17.28
3300 | [16 empty] | 3300 | [8 empty] | 3300 | 1.32 | 3087.03 | 88.77 | 8.91 | 1.25 | 3740.85 | 118.8 | 8.91 | 1.3 | 5024.52 | 177.54 | 17.82 | 1.34 | 5865 | 237.6 | 17.82 | 3300 | 1.32 | 3026.5 | 3087.03 | 88.77 | 8.91 | 3300 | 1.25 | 3667.5 | 3740.85 | 118.8 | 8.91 | 3300 | 1.3 | 4926 | 5024.52 | 177.54 | 17.82 | 3300 | 1.34 | 5750 | 5865 | 237.6 | 17.82
3400 | [16 empty] | 3400 | [8 empty] | 3400 | 1.32 | 3169.14 | 91.46 | 9.18 | 1.25 | 3838.26 | 122.4 | 9.18 | 1.31 | 5155.08 | 182.92 | 18.36 | 1.34 | 5997.6 | 244.8 | 18.36 | 3400 | 1.32 | 3107 | 3169.14 | 91.46 | 9.18 | 3400 | 1.25 | 3763 | 3838.26 | 122.4 | 9.18 | 3400 | 1.31 | 5054 | 5155.08 | 182.92 | 18.36 | 3400 | 1.34 | 5880 | 5997.6 | 244.8 | 18.36
3500 | [16 empty] | 3500 | [8 empty] | 3500 | 1.32 | 3250.74 | 94.15 | 9.45 | 1.25 | 3934.65 | 126 | 9.45 | 1.31 | 5285.13 | 188.3 | 18.9 | 1.34 | 6127.65 | 252 | 18.9 | 3500 | 1.32 | 3187 | 3250.74 | 94.15 | 9.45 | 3500 | 1.25 | 3857.5 | 3934.65 | 126 | 9.45 | 3500 | 1.31 | 5181.5 | 5285.13 | 188.3 | 18.9 | 3500 | 1.34 | 6007.5 | 6127.65 | 252 | 18.9
3600 | [16 empty] | 3600 | [8 empty] | 3600 | 1.33 | 3332.34 | 96.84 | 9.72 | 1.25 | 4031.04 | 129.6 | 9.72 | 1.31 | 5415.18 | 193.68 | 19.44 | 1.35 | 6257.7 | 259.2 | 19.44 | 3600 | 1.33 | 3267 | 3332.34 | 96.84 | 9.72 | 3600 | 1.25 | 3952 | 4031.04 | 129.6 | 9.72 | 3600 | 1.31 | 5309 | 5415.18 | 193.68 | 19.44 | 3600 | 1.35 | 6135 | 6257.7 | 259.2 | 19.44
3700 | [16 empty] | 3700 | [8 empty] | 3700 | 1.33 | 3412.92 | 99.53 | 9.99 | 1.25 | 4126.92 | 133.2 | 9.99 | 1.31 | 5544.21 | 199.06 | 19.98 | 1.35 | 6386.22 | 266.4 | 19.98 | 3700 | 1.33 | 3346 | 3412.92 | 99.53 | 9.99 | 3700 | 1.25 | 4046 | 4126.92 | 133.2 | 9.99 | 3700 | 1.31 | 5435.5 | 5544.21 | 199.06 | 19.98 | 3700 | 1.35 | 6261 | 6386.22 | 266.4 | 19.98
3800 | [16 empty] | 3800 | [8 empty] | 3800 | 1.34 | 3493.5 | 102.22 | 10.26 | 1.25 | 4222.8 | 136.8 | 10.26 | 1.32 | 5673.24 | 204.44 | 20.52 | 1.35 | 6514.74 | 273.6 | 20.52 | 3800 | 1.34 | 3425 | 3493.5 | 102.22 | 10.26 | 3800 | 1.25 | 4140 | 4222.8 | 136.8 | 10.26 | 3800 | 1.32 | 5562 | 5673.24 | 204.44 | 20.52 | 3800 | 1.35 | 6387 | 6514.74 | 273.6 | 20.52
3900 | [16 empty] | 3900 | [8 empty] | 3900 | 1.34 | 3574.08 | 104.91 | 10.53 | 1.25 | 4318.17 | 140.4 | 10.53 | 1.32 | 5800.74 | 209.82 | 21.06 | 1.35 | 6641.22 | 280.8 | 21.06 | 3900 | 1.34 | 3504 | 3574.08 | 104.91 | 10.53 | 3900 | 1.25 | 4233.5 | 4318.17 | 140.4 | 10.53 | 3900 | 1.32 | 5687 | 5800.74 | 209.82 | 21.06 | 3900 | 1.35 | 6511 | 6641.22 | 280.8 | 21.06
4000 | [16 empty] | 4000 | [8 empty] | 4000 | 1.34 | 3654.66 | 107.6 | 10.8 | 1.25 | 4413.54 | 144 | 10.8 | 1.32 | 5928.24 | 215.2 | 21.6 | 1.36 | 6767.7 | 288 | 21.6 | 4000 | 1.34 | 3583 | 3654.66 | 107.6 | 10.8 | 4000 | 1.25 | 4327 | 4413.54 | 144 | 10.8 | 4000 | 1.32 | 5812 | 5928.24 | 215.2 | 21.6 | 4000 | 1.36 | 6635 | 6767.7 | 288 | 21.6
Height [mm] | Enkelt |  | Dobbelt |  | Enkelt |  | Dobbelt |  | Enkelt |  | Dobbelt |  | Enkelt |  | Dobbelt |  | Height [mm] | Enkelt |  | Dobbelt |  | Enkelt |  | Dobbelt |  | Height [mm] | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m | n | W/m (75/65-20) | KG/m | L/m
Type | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D | Type | P5V | P5KV | P5V-D | P5KV-D | P5V | P5KV | P5V-D | P5KV-D
Length [mm] | 300 |  |  |  | 400 |  |  |  | 500 |  |  |  | 600 |  |  |  | Length [mm] | 700 | 600 |  |  | 1000 | 0
*The reduction factor is used for heat output reduction, e.g. when radiators are to be installed in trenches or under ceilings