## SC Lowline W meter
Hudevad SC Lowline
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element distance |  |  | 40 | 60 | 40 | 60
W/m at 75/65/20 |  |  | 595 | 469 | 960 | 729
n-coefficients |  |  | 1.3 | 1.3 | 1.3 | 1.3
Weight/Element |  |  | 1.1 |  | 2
Water Content/Element |  |  | 0.3 |  | 0.4
Table of heat outputs at:
Arithmetic |  |  | Logarithmic |  |  | Watt to Btu/h:
Inlet | 75 | ° C | 75 |  | 75 | 3.412
Outlet | 65 | ° C | 65 |  | 65
Ambient | 20 | ° C | 20 |  | 21
Delta T | 50 | ° C | 49.8329 |  | 48.8295
Advisory recommendation for the choice of calculation method and use of reduction factor:
Logarithmic conversion should be used on emitters up until and including height 400mm, as well as on low convectors.
The logarithmic calculation method should also be used if the relative cooling surpasses 75%.
Arithmetic conversion should be used on emitters above height 400mm if the relative cooling is under 75%.
Arithmetic outputs
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
300 | 595 | 469 | 960 | 729
Conversion to Logarithmic Outputs
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
300 | 579 | 457 | 935 | 710
Conversion to Btu/hr
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
300 | 2030.14 | 1600.228 | 3275.52 | 2487.348

## SC Lowline All sizes
Hudevad SC Lowline
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element distance |  |  | 40 | 60 | 40 | 60
W/m at 75/65/20 |  |  | 595 | 469 | 960 | 729
n-coefficients |  |  | 1.3 | 1.3 | 1.3 | 1.3
Weight/Element |  |  | 1.1 |  | 2
Water Content/Element |  |  | 0.3 |  | 0.4
Table of heat outputs at:
Arithmetic |  |  | Logarithmic |  |  | Watt to Btu/h:
Inlet | 75 | ° C | 75 |  | 75 | 3.412
Outlet | 65 | ° C | 65 |  | 65
Ambient | 20 | ° C | 20 |  | 20
Delta T | 50 | ° C | 49.8329 |  | 49.8329
Advisory recommendation for the choice of calculation method and use of reduction factor:
Logarithmic conversion should be used on emitters up until and including height 400mm, as well as on low convectors.
The logarithmic calculation method should also be used if the relative cooling surpasses 75%.
Arithmetic conversion should be used on emitters above height 400mm if the relative cooling is under 75%.
Arithmetic outputs
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element spacing |  |  | 40 | 60 | 40 | 60
Length
400 |  |  | 238 | 188 | 384 | 292
440 |  |  | 262 |  | 422
460 |  |  |  | 216 |  | 335
480 |  |  | 286 |  | 461
520 |  |  | 309 | 244 | 499 | 379
560 |  |  | 333 |  | 538
580 |  |  |  | 272 |  | 423
600 |  |  | 357 |  | 576
640 |  |  | 381 | 300 | 614 | 467
680 |  |  | 405 |  | 653
700 |  |  |  | 328 |  | 510
720 |  |  | 428 |  | 691
760 |  |  | 452 | 356 | 730 | 554
800 |  |  | 476 |  | 768
820 |  |  |  | 385 |  | 598
840 |  |  | 500 |  | 806
880 |  |  | 524 | 413 | 845 | 642
920 |  |  | 547 |  | 883
940 |  |  |  | 441 |  | 685
960 |  |  | 571 |  | 922
1000 |  |  | 595 | 469 | 960 | 729
1040 |  |  | 619 |  | 998
1060 |  |  |  | 497 |  | 773
1080 |  |  | 643 |  | 1037
1120 |  |  | 666 | 525 | 1075 | 816
1160 |  |  | 690 |  | 1114
1180 |  |  |  | 553 |  | 860
1200 |  |  | 714 |  | 1152
1240 |  |  | 738 | 582 | 1190 | 904
1280 |  |  | 762 |  | 1229
1300 |  |  |  | 610 |  | 948
1320 |  |  | 785 |  | 1267
1360 |  |  | 809 | 638 | 1306 | 991
1400 |  |  | 833 |  | 1344
1420 |  |  |  | 666 |  | 1035
1440 |  |  | 857 |  | 1382
1480 |  |  | 881 | 694 | 1421 | 1079
1520 |  |  | 904 |  | 1459
1540 |  |  |  | 722 |  | 1123
1560 |  |  | 928 |  | 1498
1600 |  |  | 952 | 750 | 1536 | 1166
1640 |  |  | 976 |  | 1574
1660 |  |  |  | 779 |  | 1210
1680 |  |  | 1000 |  | 1613
1720 |  |  | 1023 | 807 | 1651 | 1254
1760 |  |  | 1047 |  | 1690
1780 |  |  |  | 835 |  | 1298
1800 |  |  | 1071 |  | 1728
1840 |  |  | 1095 | 863 | 1766 | 1341
1880 |  |  | 1119 |  | 1805
1900 |  |  |  | 891 |  | 1385
1920 |  |  | 1142 |  | 1843
1960 |  |  | 1166 | 919 | 1882 | 1429
2000 |  |  | 1190 |  | 1920
2020 |  |  |  | 947 |  | 1473
2040 |  |  | 1214 |  | 1958
2080 |  |  | 1238 | 976 | 1997 | 1516
2120 |  |  | 1261 |  | 2035
2140 |  |  |  | 1004 |  | 1560
2160 |  |  | 1285 |  | 2074
2200 |  |  | 1309 | 1032 | 2112 | 1604
2240 |  |  | 1333 |  | 2150
2260 |  |  |  | 1060 |  | 1648
2280 |  |  | 1357 |  | 2189
2320 |  |  | 1380 | 1088 | 2227 | 1691
2360 |  |  | 1404 |  | 2266
2380 |  |  |  | 1116 |  | 1735
2400 |  |  | 1428 |  | 2304
2440 |  |  | 1452 | 1144 | 2342 | 1779
2480 |  |  | 1476 |  | 2381
2500 |  |  |  | 1173 |  | 1823
2520 |  |  | 1499 |  | 2419
2560 |  |  | 1523 | 1201 | 2458 | 1866
2600 |  |  | 1547 |  | 2496
2620 |  |  |  | 1229 |  | 1910
2640 |  |  | 1571 |  | 2534
2680 |  |  | 1595 | 1257 | 2573 | 1954
2720 |  |  | 1618 |  | 2611
2740 |  |  |  | 1285 |  | 1997
2760 |  |  | 1642 |  | 2650
2800 |  |  | 1666 | 1313 | 2688 | 2041
2840 |  |  | 1690 |  | 2726
2860 |  |  |  | 1341 |  | 2085
2880 |  |  | 1714 |  | 2765
2920 |  |  | 1737 | 1369 | 2803 | 2129
2960 |  |  | 1761 |  | 2842
2980 |  |  |  | 1398 |  | 2172
3000 |  |  | 1785 |  | 2880
Conversion to Logarithmic Outputs
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element spacing |  |  | 40 | 60 | 40 | 60
Length
400 |  |  | 238 | 188 | 384 | 292
440 |  |  | 262 |  | 422
460 |  |  |  | 216 |  | 335
480 |  |  | 286 |  | 461
520 |  |  | 309 | 244 | 499 | 379
560 |  |  | 333 |  | 538
580 |  |  |  | 272 |  | 423
600 |  |  | 357 |  | 576
640 |  |  | 381 | 300 | 614 | 467
680 |  |  | 405 |  | 653
700 |  |  |  | 328 |  | 510
720 |  |  | 428 |  | 691
760 |  |  | 452 | 356 | 730 | 554
800 |  |  | 476 |  | 768
820 |  |  |  | 385 |  | 598
840 |  |  | 500 |  | 806
880 |  |  | 524 | 413 | 845 | 642
920 |  |  | 547 |  | 883
940 |  |  |  | 441 |  | 685
960 |  |  | 571 |  | 922
1000 |  |  | 595 | 469 | 960 | 729
1040 |  |  | 619 |  | 998
1060 |  |  |  | 497 |  | 773
1080 |  |  | 643 |  | 1037
1120 |  |  | 666 | 525 | 1075 | 816
1160 |  |  | 690 |  | 1114
1180 |  |  |  | 553 |  | 860
1200 |  |  | 714 |  | 1152
1240 |  |  | 738 | 582 | 1190 | 904
1280 |  |  | 762 |  | 1229
1300 |  |  |  | 610 |  | 948
1320 |  |  | 785 |  | 1267
1360 |  |  | 809 | 638 | 1306 | 991
1400 |  |  | 833 |  | 1344
1420 |  |  |  | 666 |  | 1035
1440 |  |  | 857 |  | 1382
1480 |  |  | 881 | 694 | 1421 | 1079
1520 |  |  | 904 |  | 1459
1540 |  |  |  | 722 |  | 1123
1560 |  |  | 928 |  | 1498
1600 |  |  | 952 | 750 | 1536 | 1166
1640 |  |  | 976 |  | 1574
1660 |  |  |  | 779 |  | 1210
1680 |  |  | 1000 |  | 1613
1720 |  |  | 1023 | 807 | 1651 | 1254
1760 |  |  | 1047 |  | 1690
1780 |  |  |  | 835 |  | 1298
1800 |  |  | 1071 |  | 1728
1840 |  |  | 1095 | 863 | 1766 | 1341
1880 |  |  | 1119 |  | 1805
1900 |  |  |  | 891 |  | 1385
1920 |  |  | 1142 |  | 1843
1960 |  |  | 1166 | 919 | 1882 | 1429
2000 |  |  | 1190 |  | 1920
2020 |  |  |  | 947 |  | 1473
2040 |  |  | 1214 |  | 1958
2080 |  |  | 1238 | 976 | 1997 | 1516
2120 |  |  | 1261 |  | 2035
2140 |  |  |  | 1004 |  | 1560
2160 |  |  | 1285 |  | 2074
2200 |  |  | 1309 | 1032 | 2112 | 1604
2240 |  |  | 1333 |  | 2150
2260 |  |  |  | 1060 |  | 1648
2280 |  |  | 1357 |  | 2189
2320 |  |  | 1380 | 1088 | 2227 | 1691
2360 |  |  | 1404 |  | 2266
2380 |  |  |  | 1116 |  | 1735
2400 |  |  | 1428 |  | 2304
2440 |  |  | 1452 | 1144 | 2342 | 1779
2480 |  |  | 1476 |  | 2381
2500 |  |  |  | 1173 |  | 1823
2520 |  |  | 1499 |  | 2419
2560 |  |  | 1523 | 1201 | 2458 | 1866
2600 |  |  | 1547 |  | 2496
2620 |  |  |  | 1229 |  | 1910
2640 |  |  | 1571 |  | 2534
2680 |  |  | 1595 | 1257 | 2573 | 1954
2720 |  |  | 1618 |  | 2611
2740 |  |  |  | 1285 |  | 1997
2760 |  |  | 1642 |  | 2650
2800 |  |  | 1666 | 1313 | 2688 | 2041
2840 |  |  | 1690 |  | 2726
2860 |  |  |  | 1341 |  | 2085
2880 |  |  | 1714 |  | 2765
2920 |  |  | 1737 | 1369 | 2803 | 2129
2960 |  |  | 1761 |  | 2842
2980 |  |  |  | 1398 |  | 2172
3000 |  |  | 1785 |  | 2880
Conversion to Btu/hr
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element spacing |  |  | 40 | 60 | 40 | 60
Length
400 |  |  | 812.056 | 641.456 | 1310.208 | 996.304
440 |  |  | 893.944 |  | 1439.864
460 |  |  |  | 736.992 |  | 1143.02
480 |  |  | 975.832 |  | 1572.932
520 |  |  | 1054.308 | 832.528 | 1702.588 | 1293.148
560 |  |  | 1136.196 |  | 1835.656
580 |  |  |  | 928.064 |  | 1443.276
600 |  |  | 1218.084 |  | 1965.312
640 |  |  | 1299.972 | 1023.6 | 2094.968 | 1593.404
680 |  |  | 1381.86 |  | 2228.036
700 |  |  |  | 1119.136 |  | 1740.12
720 |  |  | 1460.336 |  | 2357.692
760 |  |  | 1542.224 | 1214.672 | 2490.76 | 1890.248
800 |  |  | 1624.112 |  | 2620.416
820 |  |  |  | 1313.62 |  | 2040.376
840 |  |  | 1706 |  | 2750.072
880 |  |  | 1787.888 | 1409.156 | 2883.14 | 2190.504
920 |  |  | 1866.364 |  | 3012.796
940 |  |  |  | 1504.692 |  | 2337.22
960 |  |  | 1948.252 |  | 3145.864
1000 |  |  | 2030.14 | 1600.228 | 3275.52 | 2487.348
1040 |  |  | 2112.028 |  | 3405.176
1060 |  |  |  | 1695.764 |  | 2637.476
1080 |  |  | 2193.916 |  | 3538.244
1120 |  |  | 2272.392 | 1791.3 | 3667.9 | 2784.192
1160 |  |  | 2354.28 |  | 3800.968
1180 |  |  |  | 1886.836 |  | 2934.32
1200 |  |  | 2436.168 |  | 3930.624
1240 |  |  | 2518.056 | 1985.784 | 4060.28 | 3084.448
1280 |  |  | 2599.944 |  | 4193.348
1300 |  |  |  | 2081.32 |  | 3234.576
1320 |  |  | 2678.42 |  | 4323.004
1360 |  |  | 2760.308 | 2176.856 | 4456.072 | 3381.292
1400 |  |  | 2842.196 |  | 4585.728
1420 |  |  |  | 2272.392 |  | 3531.42
1440 |  |  | 2924.084 |  | 4715.384
1480 |  |  | 3005.972 | 2367.928 | 4848.452 | 3681.548
1520 |  |  | 3084.448 |  | 4978.108
1540 |  |  |  | 2463.464 |  | 3831.676
1560 |  |  | 3166.336 |  | 5111.176
1600 |  |  | 3248.224 | 2559 | 5240.832 | 3978.392
1640 |  |  | 3330.112 |  | 5370.488
1660 |  |  |  | 2657.948 |  | 4128.52
1680 |  |  | 3412 |  | 5503.556
1720 |  |  | 3490.476 | 2753.484 | 5633.212 | 4278.648
1760 |  |  | 3572.364 |  | 5766.28
1780 |  |  |  | 2849.02 |  | 4428.776
1800 |  |  | 3654.252 |  | 5895.936
1840 |  |  | 3736.14 | 2944.556 | 6025.592 | 4575.492
1880 |  |  | 3818.028 |  | 6158.66
1900 |  |  |  | 3040.092 |  | 4725.62
1920 |  |  | 3896.504 |  | 6288.316
1960 |  |  | 3978.392 | 3135.628 | 6421.384 | 4875.748
2000 |  |  | 4060.28 |  | 6551.04
2020 |  |  |  | 3231.164 |  | 5025.876
2040 |  |  | 4142.168 |  | 6680.696
2080 |  |  | 4224.056 | 3330.112 | 6813.764 | 5172.592
2120 |  |  | 4302.532 |  | 6943.42
2140 |  |  |  | 3425.648 |  | 5322.72
2160 |  |  | 4384.42 |  | 7076.488
2200 |  |  | 4466.308 | 3521.184 | 7206.144 | 5472.848
2240 |  |  | 4548.196 |  | 7335.8
2260 |  |  |  | 3616.72 |  | 5622.976
2280 |  |  | 4630.084 |  | 7468.868
2320 |  |  | 4708.56 | 3712.256 | 7598.524 | 5769.692
2360 |  |  | 4790.448 |  | 7731.592
2380 |  |  |  | 3807.792 |  | 5919.82
2400 |  |  | 4872.336 |  | 7861.248
2440 |  |  | 4954.224 | 3903.328 | 7990.904 | 6069.948
2480 |  |  | 5036.112 |  | 8123.972
2500 |  |  |  | 4002.276 |  | 6220.076
2520 |  |  | 5114.588 |  | 8253.628
2560 |  |  | 5196.476 | 4097.812 | 8386.696 | 6366.792
2600 |  |  | 5278.364 |  | 8516.352
2620 |  |  |  | 4193.348 |  | 6516.92
2640 |  |  | 5360.252 |  | 8646.008
2680 |  |  | 5442.14 | 4288.884 | 8779.076 | 6667.048
2720 |  |  | 5520.616 |  | 8908.732
2740 |  |  |  | 4384.42 |  | 6813.764
2760 |  |  | 5602.504 |  | 9041.8
2800 |  |  | 5684.392 | 4479.956 | 9171.456 | 6963.892
2840 |  |  | 5766.28 |  | 9301.112
2860 |  |  |  | 4575.492 |  | 7114.02
2880 |  |  | 5848.168 |  | 9434.18
2920 |  |  | 5926.644 | 4671.028 | 9563.836 | 7264.148
2960 |  |  | 6008.532 |  | 9696.904
2980 |  |  |  | 4769.976 |  | 7410.864
3000 |  |  | 6090.42 |  | 9826.56