## SC Lowline W meter
Hudevad SC Lowline
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element distance |  |  | 40 | 60 | 40 | 60
W/m at 75/65/20 |  |  | 595 | 469 | 960 | 729
n-coefficients |  |  | 1.3 | 1.3 | 1.3 | 1.3
Weight/Element |  |  | 1.1 |  | 2
Water Content/Element |  |  | 0.3 |  | 0.4
Table of heat outputs at:
Arithmetic |  |  | Logarithmic |  |  | Watt to Btu/h:
Inlet | 75 | ° C | 75 |  | 75 | 3.412
Outlet | 65 | ° C | 65 |  | 65
Ambient | 20 | ° C | 20 |  | 21
Delta T | 50 | ° C | 49.8329 |  | 48.8295
Advisory recommendation for the choice of calculation method and use of reduction factor:
Logarithmic conversion should be used on emitters up until and including height 400mm, as well as on low convectors.
The logarithmic calculation method should also be used if the relative cooling surpasses 75%.
Arithmetic conversion should be used on emitters above height 400mm if the relative cooling is under 75%.
Arithmetic outputs
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
300 | 595 | 469 | 960 | 729
Conversion to Logarithmic Outputs
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
300 | 579 | 457 | 935 | 710
Conversion to Btu/hr
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
300 | 2030.14 | 1600.228 | 3275.52 | 2487.348

## SC Lowline All sizes
Hudevad SC Lowline
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element distance |  |  | 40 | 60 | 40 | 60
W/m at 75/65/20 |  |  | 595 | 469 | 960 | 729
n-coefficients |  |  | 1.3 | 1.3 | 1.3 | 1.3
Weight/Element |  |  | 1.1 |  | 2
Water Content/Element |  |  | 0.3 |  | 0.4
Table of heat outputs at:
Arithmetic |  |  | Logarithmic |  |  | Watt to Btu/h:
Inlet | 75 | ° C | 75 |  | 60 | 3.412
Outlet | 65 | ° C | 65 |  | 40
Ambient | 20 | ° C | 20 |  | 20
Delta T | 50 | ° C | 49.8329 |  | 28.8539
Advisory recommendation for the choice of calculation method and use of reduction factor:
Logarithmic conversion should be used on emitters up until and including height 400mm, as well as on low convectors.
The logarithmic calculation method should also be used if the relative cooling surpasses 75%.
Arithmetic conversion should be used on emitters above height 400mm if the relative cooling is under 75%.
Arithmetic outputs
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element spacing |  |  | 40 | 60 | 40 | 60
Length
80 |  |  | 48 |  | 77
100 |  |  |  | 47 |  | 73
120 |  |  | 71 |  | 115
160 |  |  | 95 | 75 | 154 | 117
200 |  |  | 119 |  | 192
220 |  |  |  | 103 |  | 160
240 |  |  | 143 |  | 230
280 |  |  | 167 | 131 | 269 | 204
320 |  |  | 190 |  | 307
340 |  |  |  | 159 |  | 248
360 |  |  | 214 |  | 346
400 |  |  | 238 | 188 | 384 | 292
440 |  |  | 262 |  | 422
460 |  |  |  | 216 |  | 335
480 |  |  | 286 |  | 461
520 |  |  | 309 | 244 | 499 | 379
560 |  |  | 333 |  | 538
580 |  |  |  | 272 |  | 423
600 |  |  | 357 |  | 576
640 |  |  | 381 | 300 | 614 | 467
680 |  |  | 405 |  | 653
700 |  |  |  | 328 |  | 510
720 |  |  | 428 |  | 691
760 |  |  | 452 | 356 | 730 | 554
800 |  |  | 476 |  | 768
820 |  |  |  | 385 |  | 598
840 |  |  | 500 |  | 806
880 |  |  | 524 | 413 | 845 | 642
920 |  |  | 547 |  | 883
940 |  |  |  | 441 |  | 685
960 |  |  | 571 |  | 922
1000 |  |  | 595 | 469 | 960 | 729
1040 |  |  | 619 |  | 998
1060 |  |  |  | 497 |  | 773
1080 |  |  | 643 |  | 1037
1120 |  |  | 666 | 525 | 1075 | 816
1160 |  |  | 690 |  | 1114
1180 |  |  |  | 553 |  | 860
1200 |  |  | 714 |  | 1152
1240 |  |  | 738 | 582 | 1190 | 904
1280 |  |  | 762 |  | 1229
1300 |  |  |  | 610 |  | 948
1320 |  |  | 785 |  | 1267
1360 |  |  | 809 | 638 | 1306 | 991
1400 |  |  | 833 |  | 1344
1420 |  |  |  | 666 |  | 1035
1440 |  |  | 857 |  | 1382
1480 |  |  | 881 | 694 | 1421 | 1079
1520 |  |  | 904 |  | 1459
1540 |  |  |  | 722 |  | 1123
1560 |  |  | 928 |  | 1498
1600 |  |  | 952 | 750 | 1536 | 1166
1640 |  |  | 976 |  | 1574
1660 |  |  |  | 779 |  | 1210
1680 |  |  | 1000 |  | 1613
1720 |  |  | 1023 | 807 | 1651 | 1254
1760 |  |  | 1047 |  | 1690
1780 |  |  |  | 835 |  | 1298
1800 |  |  | 1071 |  | 1728
1840 |  |  | 1095 | 863 | 1766 | 1341
1880 |  |  | 1119 |  | 1805
1900 |  |  |  | 891 |  | 1385
1920 |  |  | 1142 |  | 1843
1960 |  |  | 1166 | 919 | 1882 | 1429
2000 |  |  | 1190 |  | 1920
2020 |  |  |  | 947 |  | 1473
2040 |  |  | 1214 |  | 1958
2080 |  |  | 1238 | 976 | 1997 | 1516
2120 |  |  | 1261 |  | 2035
2140 |  |  |  | 1004 |  | 1560
2160 |  |  | 1285 |  | 2074
2200 |  |  | 1309 | 1032 | 2112 | 1604
2240 |  |  | 1333 |  | 2150
2260 |  |  |  | 1060 |  | 1648
2280 |  |  | 1357 |  | 2189
2320 |  |  | 1380 | 1088 | 2227 | 1691
2360 |  |  | 1404 |  | 2266
2380 |  |  |  | 1116 |  | 1735
2400 |  |  | 1428 |  | 2304
2440 |  |  | 1452 | 1144 | 2342 | 1779
2480 |  |  | 1476 |  | 2381
2500 |  |  |  | 1173 |  | 1823
2520 |  |  | 1499 |  | 2419
2560 |  |  | 1523 | 1201 | 2458 | 1866
2600 |  |  | 1547 |  | 2496
2620 |  |  |  | 1229 |  | 1910
2640 |  |  | 1571 |  | 2534
2680 |  |  | 1595 | 1257 | 2573 | 1954
2720 |  |  | 1618 |  | 2611
2740 |  |  |  | 1285 |  | 1997
2760 |  |  | 1642 |  | 2650
2800 |  |  | 1666 | 1313 | 2688 | 2041
2840 |  |  | 1690 |  | 2726
2860 |  |  |  | 1341 |  | 2085
2880 |  |  | 1714 |  | 2765
2920 |  |  | 1737 | 1369 | 2803 | 2129
2960 |  |  | 1761 |  | 2842
2980 |  |  |  | 1398 |  | 2172
3000 |  |  | 1785 |  | 2880
Conversion to Logarithmic Outputs
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element spacing |  |  | 40 | 60 | 40 | 60
Length
80 |  |  | 23 |  | 38
100 |  |  |  | 23 |  | 36
120 |  |  | 35 |  | 57
160 |  |  | 47 | 37 | 75 | 57
200 |  |  | 58 |  | 94
220 |  |  |  | 51 |  | 79
240 |  |  | 70 |  | 113
280 |  |  | 82 | 65 | 132 | 100
320 |  |  | 94 |  | 151
340 |  |  |  | 78 |  | 122
360 |  |  | 105 |  | 170
400 |  |  | 117 | 92 | 189 | 143
440 |  |  | 129 |  | 208
460 |  |  |  | 106 |  | 165
480 |  |  | 140 |  | 226
520 |  |  | 152 | 120 | 245 | 186
560 |  |  | 164 |  | 264
580 |  |  |  | 134 |  | 208
600 |  |  | 175 |  | 283
640 |  |  | 187 | 148 | 302 | 229
680 |  |  | 199 |  | 321
700 |  |  |  | 161 |  | 251
720 |  |  | 211 |  | 340
760 |  |  | 222 | 175 | 359 | 272
800 |  |  | 234 |  | 377
820 |  |  |  | 189 |  | 294
840 |  |  | 246 |  | 396
880 |  |  | 257 | 203 | 415 | 315
920 |  |  | 269 |  | 434
940 |  |  |  | 217 |  | 337
960 |  |  | 281 |  | 453
1000 |  |  | 292 | 230 | 472 | 358
1040 |  |  | 304 |  | 491
1060 |  |  |  | 244 |  | 380
1080 |  |  | 316 |  | 510
1120 |  |  | 328 | 258 | 528 | 401
1160 |  |  | 339 |  | 547
1180 |  |  |  | 272 |  | 423
1200 |  |  | 351 |  | 566
1240 |  |  | 363 | 286 | 585 | 444
1280 |  |  | 374 |  | 604
1300 |  |  |  | 300 |  | 466
1320 |  |  | 386 |  | 623
1360 |  |  | 398 | 313 | 642 | 487
1400 |  |  | 409 |  | 661
1420 |  |  |  | 327 |  | 509
1440 |  |  | 421 |  | 679
1480 |  |  | 433 | 341 | 698 | 530
1520 |  |  | 444 |  | 717
1540 |  |  |  | 355 |  | 552
1560 |  |  | 456 |  | 736
1600 |  |  | 468 | 369 | 755 | 573
1640 |  |  | 480 |  | 774
1660 |  |  |  | 383 |  | 595
1680 |  |  | 491 |  | 793
1720 |  |  | 503 | 396 | 812 | 616
1760 |  |  | 515 |  | 830
1780 |  |  |  | 410 |  | 638
1800 |  |  | 526 |  | 849
1840 |  |  | 538 | 424 | 868 | 659
1880 |  |  | 550 |  | 887
1900 |  |  |  | 438 |  | 681
1920 |  |  | 561 |  | 906
1960 |  |  | 573 | 452 | 925 | 702
2000 |  |  | 585 |  | 944
2020 |  |  |  | 466 |  | 724
2040 |  |  | 597 |  | 962
2080 |  |  | 608 | 479 | 981 | 745
2120 |  |  | 620 |  | 1000
2140 |  |  |  | 493 |  | 767
2160 |  |  | 632 |  | 1019
2200 |  |  | 643 | 507 | 1038 | 788
2240 |  |  | 655 |  | 1057
2260 |  |  |  | 521 |  | 810
2280 |  |  | 667 |  | 1076
2320 |  |  | 678 | 535 | 1095 | 831
2360 |  |  | 690 |  | 1113
2380 |  |  |  | 549 |  | 853
2400 |  |  | 702 |  | 1132
2440 |  |  | 714 | 562 | 1151 | 874
2480 |  |  | 725 |  | 1170
2500 |  |  |  | 576 |  | 896
2520 |  |  | 737 |  | 1189
2560 |  |  | 749 | 590 | 1208 | 917
2600 |  |  | 760 |  | 1227
2620 |  |  |  | 604 |  | 939
2640 |  |  | 772 |  | 1246
2680 |  |  | 784 | 618 | 1264 | 960
2720 |  |  | 795 |  | 1283
2740 |  |  |  | 632 |  | 982
2760 |  |  | 807 |  | 1302
2800 |  |  | 819 | 645 | 1321 | 1003
2840 |  |  | 830 |  | 1340
2860 |  |  |  | 659 |  | 1025
2880 |  |  | 842 |  | 1359
2920 |  |  | 854 | 673 | 1378 | 1046
2960 |  |  | 866 |  | 1397
2980 |  |  |  | 687 |  | 1068
3000 |  |  | 877 |  | 1415
Conversion to Btu/hr
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element spacing |  |  | 40 | 60 | 40 | 60
Length
80 |  |  | 163.776 |  | 262.724
100 |  |  |  | 160.364 |  | 249.076
120 |  |  | 242.252 |  | 392.38
160 |  |  | 324.14 | 255.9 | 525.448 | 399.204
200 |  |  | 406.028 |  | 655.104
220 |  |  |  | 351.436 |  | 545.92
240 |  |  | 487.916 |  | 784.76
280 |  |  | 569.804 | 446.972 | 917.828 | 696.048
320 |  |  | 648.28 |  | 1047.484
340 |  |  |  | 542.508 |  | 846.176
360 |  |  | 730.168 |  | 1180.552
400 |  |  | 812.056 | 641.456 | 1310.208 | 996.304
440 |  |  | 893.944 |  | 1439.864
460 |  |  |  | 736.992 |  | 1143.02
480 |  |  | 975.832 |  | 1572.932
520 |  |  | 1054.308 | 832.528 | 1702.588 | 1293.148
560 |  |  | 1136.196 |  | 1835.656
580 |  |  |  | 928.064 |  | 1443.276
600 |  |  | 1218.084 |  | 1965.312
640 |  |  | 1299.972 | 1023.6 | 2094.968 | 1593.404
680 |  |  | 1381.86 |  | 2228.036
700 |  |  |  | 1119.136 |  | 1740.12
720 |  |  | 1460.336 |  | 2357.692
760 |  |  | 1542.224 | 1214.672 | 2490.76 | 1890.248
800 |  |  | 1624.112 |  | 2620.416
820 |  |  |  | 1313.62 |  | 2040.376
840 |  |  | 1706 |  | 2750.072
880 |  |  | 1787.888 | 1409.156 | 2883.14 | 2190.504
920 |  |  | 1866.364 |  | 3012.796
940 |  |  |  | 1504.692 |  | 2337.22
960 |  |  | 1948.252 |  | 3145.864
1000 |  |  | 2030.14 | 1600.228 | 3275.52 | 2487.348
1040 |  |  | 2112.028 |  | 3405.176
1060 |  |  |  | 1695.764 |  | 2637.476
1080 |  |  | 2193.916 |  | 3538.244
1120 |  |  | 2272.392 | 1791.3 | 3667.9 | 2784.192
1160 |  |  | 2354.28 |  | 3800.968
1180 |  |  |  | 1886.836 |  | 2934.32
1200 |  |  | 2436.168 |  | 3930.624
1240 |  |  | 2518.056 | 1985.784 | 4060.28 | 3084.448
1280 |  |  | 2599.944 |  | 4193.348
1300 |  |  |  | 2081.32 |  | 3234.576
1320 |  |  | 2678.42 |  | 4323.004
1360 |  |  | 2760.308 | 2176.856 | 4456.072 | 3381.292
1400 |  |  | 2842.196 |  | 4585.728
1420 |  |  |  | 2272.392 |  | 3531.42
1440 |  |  | 2924.084 |  | 4715.384
1480 |  |  | 3005.972 | 2367.928 | 4848.452 | 3681.548
1520 |  |  | 3084.448 |  | 4978.108
1540 |  |  |  | 2463.464 |  | 3831.676
1560 |  |  | 3166.336 |  | 5111.176
1600 |  |  | 3248.224 | 2559 | 5240.832 | 3978.392
1640 |  |  | 3330.112 |  | 5370.488
1660 |  |  |  | 2657.948 |  | 4128.52
1680 |  |  | 3412 |  | 5503.556
1720 |  |  | 3490.476 | 2753.484 | 5633.212 | 4278.648
1760 |  |  | 3572.364 |  | 5766.28
1780 |  |  |  | 2849.02 |  | 4428.776
1800 |  |  | 3654.252 |  | 5895.936
1840 |  |  | 3736.14 | 2944.556 | 6025.592 | 4575.492
1880 |  |  | 3818.028 |  | 6158.66
1900 |  |  |  | 3040.092 |  | 4725.62
1920 |  |  | 3896.504 |  | 6288.316
1960 |  |  | 3978.392 | 3135.628 | 6421.384 | 4875.748
2000 |  |  | 4060.28 |  | 6551.04
2020 |  |  |  | 3231.164 |  | 5025.876
2040 |  |  | 4142.168 |  | 6680.696
2080 |  |  | 4224.056 | 3330.112 | 6813.764 | 5172.592
2120 |  |  | 4302.532 |  | 6943.42
2140 |  |  |  | 3425.648 |  | 5322.72
2160 |  |  | 4384.42 |  | 7076.488
2200 |  |  | 4466.308 | 3521.184 | 7206.144 | 5472.848
2240 |  |  | 4548.196 |  | 7335.8
2260 |  |  |  | 3616.72 |  | 5622.976
2280 |  |  | 4630.084 |  | 7468.868
2320 |  |  | 4708.56 | 3712.256 | 7598.524 | 5769.692
2360 |  |  | 4790.448 |  | 7731.592
2380 |  |  |  | 3807.792 |  | 5919.82
2400 |  |  | 4872.336 |  | 7861.248
2440 |  |  | 4954.224 | 3903.328 | 7990.904 | 6069.948
2480 |  |  | 5036.112 |  | 8123.972
2500 |  |  |  | 4002.276 |  | 6220.076
2520 |  |  | 5114.588 |  | 8253.628
2560 |  |  | 5196.476 | 4097.812 | 8386.696 | 6366.792
2600 |  |  | 5278.364 |  | 8516.352
2620 |  |  |  | 4193.348 |  | 6516.92
2640 |  |  | 5360.252 |  | 8646.008
2680 |  |  | 5442.14 | 4288.884 | 8779.076 | 6667.048
2720 |  |  | 5520.616 |  | 8908.732
2740 |  |  |  | 4384.42 |  | 6813.764
2760 |  |  | 5602.504 |  | 9041.8
2800 |  |  | 5684.392 | 4479.956 | 9171.456 | 6963.892
2840 |  |  | 5766.28 |  | 9301.112
2860 |  |  |  | 4575.492 |  | 7114.02
2880 |  |  | 5848.168 |  | 9434.18
2920 |  |  | 5926.644 | 4671.028 | 9563.836 | 7264.148
2960 |  |  | 6008.532 |  | 9696.904
2980 |  |  |  | 4769.976 |  | 7410.864
3000 |  |  | 6090.42 |  | 9826.56
Hudevad Radiator Design A/S
Ambolten 37
DK-6000 Kolding
Tel. +45 7542 0255